## ReadMe
ITRC PFAS Technical and Regulatory Guidance Document
Table 15-1 PFAS Case Study Summary Table
The ITRC intends to update this table periodically as new information is gathered. The user is encouraged to visit the ITRC PFAS web page (http://pfas-1.itrcweb.org) to access the current version of this file.
Users who identify potential additions to the material in this table are encouraged to send that information to itrc@itrcweb.org
April 2020
See ITRC Disclaimer http://pfas-1.itrcweb.org/about-itrc/#disclaimer

## Table 15-1 Case Study Table
ITRC PFAS Case Study Table
April 2020
Case Study No.1 | Type of Water Treatment System | Treatment Technology | Process Flow Rate (gallons per minute) | Description of Treatment System | Representative PFAS Influent Concentrations (parts per trillion) | PFAS Breakthrough Times3 | Co-Contaminants | Discharge Objectives for Individual PFAS | Treatment Effectiveness for Nonsorption Technologies (e.g., % removed or destroyed) | Typical Adsorption Unit Change-Out Frequency (months) | Adsorption Media Change-Out Driver (Individual PFAS and Change-Out Criteria) | System Status and Operating Timeframe to Date
A. Bituminous Granular Activated Carbon (GAC) Systems
1 | Potable Water System | Bituminous GAC | 425 | (4) 10-ft dia GAC units (20,000 lbs each); (2) sets of parallel lead-lag configuration | PFOA: 1,800 - 14,000 | Information not available | None reported | 15 ppt PFOA | NA | Estimated 2-3 months | Prescheduled | Operational since Nov 2007
2 | Potable Water System | Bituminous GAC | 140 | (2) 10-ft dia GAC units (20,000 lbs each) in lead-lag configuration | PFOA: 1,830; PFOS: 1,150 | Not provided, since change-out criteria is less than breakthrough definition | TCE: 77 ug/L | 70 ppt total PFOA+PFOS | NA | Approximately once per year over current operating history | PFOA+PFOS > 70 ppt at discharge of lead unit | GAC system installed for TCE treatment in 1993. Monitoring for PFOA/PFOS began in 2014, and incorporated into the NPDES permit in July 2018.
3 | Groundwater | 8 x 40 Mesh Thermally Regenerated (Pooled) Bituminous GAC | 225 | (2) 10-ft dia GAC units (20,000 lbs each) in lead-lag configuration | PFOA: 1,000; PFOS: 3,700 | Not provided | None reported | 40 ppt PFOA; 20 ppt PFOS | NA | 3 months | Not provided | Operational since April 2015
4 | Potable Water System | 12 x 40 Mesh Virgin Bituminous GAC | 1500 | (6) 10-ft dia GAC units (20,000 lbs each); (3) sets of parallel lead-lag configuration | PFOA + PFOS: 1,000 | PFOA and PFOS breakthrough at 12-18 months | TOC 1-2 mg/L | 70 ppt total PFOA+PFOS | NA | 12 to 18 months | PFOA+PFOS > 70 ppt after lead vessel | Operational since December 2016
5 | Potable Water System | Virgin Bituminous GAC (considering use of thermally regenerated GAC) | 2000 | (6) 10-ft dia GAC units (20,000 lbs each); (3) sets of parallel lead-lag configuration | PFBA, PFBS, PFPeA, PFHxA, PFOA, PFHps: 5-25; PFHxS, PFOS: 170-270 | PFBA: 5 months; PFPeA: 8 months; PFHxA: 11 months | 1 ug/L chloroform; 0.55 mg/L TOC | 70 ppt total PFOA+PFOS | NA | No change-outs at time of data collection; initial vendor estimate of once per year | Not identified | Operational since June 2017
6 | Potable Water System | Virgin Bituminous GAC | 500 | (4) 8-ft dia GAC units (12,000 lbs each); (2) sets of parallel lead-lag configuration | PFBA, PFBS, PFNA, PFHpA, PFDA: 8-25; PFHxA, PFPeA, PFOS, PFHxS: 30-50; PFOA: 70-100 | No breakthrough measured at time of data collection | None reported | 70 ppt total PFOA+PFOS | NA | No change-outs at time of data collection | Not identified | Operational since June 2018
7 | Potable Water System | Virgin Bituminous GAC | 800 | (4) 10-ft dia GAC units (20,000 lbs each); (2) sets of parallel lead-lag configuration | PFBA, PFBS, PFNA, PFHpA, PFOA: 2-25; PFHxA, PFPeA, PFOS: 30-50; PFHxS: 120 | PFBA: 5 months | None reported | 70 ppt total PFOA+PFOS | NA | No change-outs at time of data collection | Not identified | Operational since March 2018
10 | Potable Water System | 12 x 40 Mesh Virgin Bituminous GAC | 350 | (2) 12-ft dia GAC units in series (40,000 lbs each) | PFOA: 500; PFOS 300 | PFOA and PFOS breakthrough at 12-18 months | None reported | 70 ppt total PFOA+PFOS | NA | 12 to 18 months | 25% of influent concentration after lead vessel | Operational since July 2015
11 | Potable Water System | 8 x 30 Mesh Thermally Regenerated Bituminus GAC | 3200 | (11) 10-ft dia GAC units (20,000 lbs each); lead-only configuration | PFBS, PFNA, PFHpA: 3-15; PFOS: 60; PFOA, PFHxS: 100-200 | PFBS, PFHpA: 6 months; PFNA, PFHxS, PFOA: 9 months | TCE 1-3 ug/L | Nondetect all PFAS | NA | Once per year for all GAC units | Detection of PFOA or PFOS above reporting limits; annual change-outs typically prescheduled | GAC system installed for TCE treatment in 2003. Monitoring for PFOA/PFOS began in 2015.
B. Coconut GAC Systems
1 | Potable Water System | 12 x 30 Mesh Coconut GAC | 15 | (2) 15-inch units in lead-lag configuration | PFBA & PFHpA: 1-25; PFBS, PFHxA, PFPeA, PFOA: 25-50; PFHxS, PFOS: 700-1,000 | No breakthrough measured at time of data collection | None reported | 70 ppt total PFOA+PFOS | NA | One change-out of both units every 6 months; three change-outs peformed at time of data collection | Prescheduled | Operational since February 2017; converted to public water supply in late 2018
2 | Potable Water System | 12 x 30 Mesh Coconut GAC | 80 | (12) 15-inch dia GAC units; (6) sets of parallel lead-lag configuration | PFBA, PFBS, PFHpA, PFHxA, PFOA: 1-30; PFHxS, PFPeA, PFOS: 50-100 | PFPeA: 3 months; PFBA, PFHxS, PFHxA: 4 months | None reported | 70 ppt total PFOA+PFOS | NA | Change-out of all units every 6 months; three change-outs peformed at time of data collection | Prescheduled | Operational since January 2017; converted to public water supply in late 2018
C. Ion Exchange Resin (IX) Systems
1 | Potable Water System | PFAS-Selective Single-Use IX | 185 | (2) 5-ft dia IX vessels (100 ft3 each) in lead-lag configuration | PFOA: 234; PFOS: 648; PFBS: 33; PFHxA: 141; PFHpA: 52; PFHxS: 316; PFNA 10 | PFXA: 8 months; PFHpA: 19 months; PFOA: 30 months; PFNA, PFBS, PFHxS, PFOS: > 41 months (based on long-term pilot study data) | Total VOCs (TCE, PCE): 230 ug/L; TOC: 0.7 mg/L | PFOA and PFOS both 2.5 ppt | NA | No change-outs at time of data collection | Any detection of a Method 537 PFAS compound at effluent of lag vessel | Pilot system operating since mid-2016; full-scale operation since August 2018
3 | Potable Water System | PFAS-Selective Single-Use IX | 1100 | (6) 6-ft dia IX units (130 ft3 each) in series; (3) sets of parallel lead-lag configuration | PFHpA, PFBA, PFBS:25-65; PFOA, PFOS, PFPeA: 85-100; PFHxA: 180; PFHxS: 300 | PFBA: 2 months; PFpeA: 9 months; PFHxA: breakthrough 15-18% after one year | None reported | 70 ppt total PFOA+PFOS | NA | No change-outs at time of data collection | Not identified | Operational since July 2018
4 | Nonpotable Water Wells | PFAS-Selective Single-Use IX | 600 | (2) 6-ft dia IX units (120 ft3 each) in lead-lag configuration | PFOA: 26; PFOS: 165; PFBA 11; PFBS: 7; PFHxA 27 | No breakthrough measured at time of data collection | TOC: 1 mg/L | 70 ppt total PFOA+PFOS | NA | No change-outs at time of data collection | Not identified | Operational since August 2018
5 | Potable Water System | PFAS-Selective Regenerable Use IX followed by PFAS-Selective Single-Use IX | 200 | Multi-media filter for TSS; IX unit for TOC and Fe pretreatment; (4) 3-ft dia regenerable IX units (35 ft3 each) followed by (2) 5-ft dia single-use IX units (111 ft3 each); (2) sets of parallel lead-lag configuration | Total PFAS: 50,000; PFOS+ PFHxS: 45,000; PFOA: 500 | PFPeA and PFHxA detected >10 ppt after lead vessel at 6 months, followed by PFOA at 7 months | TOC: 5 mg/L; Iron: 0.2-0.3 mg/L; TSS: 1-3 mg/L | 1 ppt for combined Method 529 PFAS | TOC: > 80% removal Iron: 90% removal Effluent TSS: nondetect | Prescheduled regeneration of lead IX vessel every 2 months | IX resin regeneration driver for lead units is increasing trend of PFOS, PFOA, or PFHxS in the effluent OR every 2 months | Operational since June 2018
D. Combined GAC-IX Systems
1 | Potable Water System | 8 x 30 Mesh Virgin Bituminous GAC followed by PFAS-Selective Single-Use IX | 50 | (2) Bituminous GAC units (600 lbs each) followed by (1) IX unit (20 ft3). System was later replaced with (2) IX units in lead-lag configuration | PFOS: 55; PFOA: 27; PFBS: 8; PFHxA: 10; PFHpA: 5; PFHxS 36 | GAC breakthrough of lead unit at 70 days; IX breakthrough of polishing unit at 450 days | TOC: 0.5 mg/L | PFOA and PFOS both 2.5 ppt | NA | 21 months for IX | >2.5 ppt of PFOA or PFOS at effluent of lag IX vessel | Initial system operated from November 2016 to October 2018. Replacement system started operating in October 2018 and has been changed to entirely IX.
2 | Stormwater Runoff Pond | 8 x C330 Mesh Thermally Reactivated Bituminous GAC followed by PFAS-Selective Single-Use IX | 300 | (2) 6 ft dia GAC units (5,000 lbs each) followed by (2) 6 ft dia IX units (120 ft3 each); (2) sets of parallel lead-lag configuration | PFBS, PFDA, PFNA: 5-10; PFBA, PFHpA, PFOA: 10-30; 62FTS, PFHxA, PFHxS, PFPeA: 30-50; PFOS: 250 | PFBA, PFHpA, PFHxA, PFHxS, PFPA, PFOS: 3-4 months for lead GAC unit (severe algae and biofouling issues skewed data towards shorter definition breakthrough times) | None reported | None (treated pond water used for golf course irrigation); target is nondetect for all Method 529 PFAS | NA | Once per year for lead GAC units to date | Annual change-out of lead GAC units prescheduled; or minimal removal occuring | Operational since June 2018
E. Reverse Osmosis (RO) Systems
1 | Potable Water System | Reverse Osmosis | 60000 | Microfilter, RO, advanced oxidation, decarbonation, lime addition. RO units (15) (14 operational, 1 standby), 3,500 gpm each | PFPnA: 10; PFHxA: 19; PFHpA: 3; PFOA: 11; PFNA: 4; PFDA: 2; PFUnA: <1; PFBS: 4; PFHxS 5; PFOS: 14 | NA | Conventional parameters consistent with treated secondary effluent | NA | Effluent concentrations: PFAS measured in influent treated to below analytical reporting limits | NA | NA | Short-term study of existing POTW
2 | Potable Water System | Reverse Osmosis | 750 | Microfilter, reverse osmosis, hydrogen peroxide addition, ultraviolet light | PFPnA: 10; PFHxA: 19; PFHpA: 3; PFOA: 11; PFNA: 4; PFDA: 2; PFUnA: <1 | NA | Conventional parameters consistent with treated secondary effluent | NA | Effluent concentrations: PFAS measured in influent treated to below analytical reporting limits | NA | NA | Short-term study of existing POTW
Notes:
1) Case study information and data were provided from multiple sources and represent varying operational time frames and number of sampling events, etc. PFAS treatment case study
information has been included to provide readers with some general knowledge and awareness of early treatment applications. These case studies are different from those presented in section 15.2.
2) Site names and locations have been kept anonymous at the request of the parties that were willing to provide PFAS case study treatment data for ongoing applications.
The case study information included in this table has not been published in any reference materials or periodicals, and is mostly unavailable in accessible public databases.
3) For purposes of the case study data compilation, the ITRC work team has defined PFAS breakthrough time as the concentration after the lead unit
being consistently greater than 25% of the influent concentration, or based on professional judgment of either the original sources of the data
or ITRC PFAS work team members compiling the treatment data. This is a mostly subjective determination meant strictly for information purposes to the readers,
and should not be interpreted as being based on any kind of statistical definition or analysis that has undergone any kind of rigorous peer review process.
Note on C8: Joy Drohan: Do dimensions need a unit? I'm not sure offhand what it'd likely be. Microns? Next cell too, and bleow.